## Slide 1
  Proportional Integral Differential (PID)
    Most common type of controller
    e.g. Cruise Control
    Set Point – desired value of output
    Error – difference between set point and current output (process variable)
PID - is a control loop feedback mechanism widely used in a variety of applications requiring continuously modulated control. A PID controller continuously calculates an error value e (t) as the difference between a desired set point (SP) and a measured process variable (PV) and applies a correction based on proportional, integral and differential error terms.
1

## Slide 2
Proportional Control
  Sometimes used alone
  Error: e(t) = sp(t) – measured(t)
  P Term: P =
  Correction diminishes as error goes to zero
  if is small, error decreases slowly
  If , pv(t) overshoots
  Steady state error not zero
1

## Slide 3
Differential Control
  Estimate of future trend
  Error: e(t) = sp(t) – measured(t)
  Δ e(t) = )
  D = * Δ e(t) / Δ t
  Damps Overshoot
  If is large, error decreases slowly
  If , pv(t) overshoots
  Problems
    Can exacerbate noise if output not filtered
    Derivative term normally small compared to proportional term
    For differentially steered robot, Kd is larger.
1

## Slide 4
Integral Control
  I corrects residual offset errors
  PI controller, e.g. for line following
  Error: e(t) = sp(t) – measure(t)
  I = I + e(t) * Δt
  Problem of Integral Windup
    If ramping up set point
    Disable until in controllable region
    Set bounds
    Reset for new set point
Integral Windup - refers to the situation in a PID controller where a large change in set point occurs and the integral term accumulates a significant error during the change, thus overshooting and continuing to increase as the accumulated error is offset by errors in the other direction.
2

## Slide 5
Tuning
  Setting PID coefficients somewhat of an art
  Trial and error; tuning formulas; auto tuners
  Start with P, add I, add D last
  PID has many refinements